## Calculator
Water Demand, LPCD, and Peak Factors
Compute average daily, max daily, peak hour, and design flow for the 30-year horizon. Includes fire demand (Kuichling) and UFW allowance per CPHEEO Chapter 3.
Generated by InfraLens · https://infralens.in/cpheeo · Based on CPHEEO Manual on Water Supply & Treatment (Govt of India, MoHUA)
INPUTS | VALUE | UNIT | HELP
Design population | 100000 | persons
Per-capita supply | 135 | LPCD | 135 urban+sewer, 70 urban, 55 rural (JJM/BIS 1172:2012)
Max day / avg day factor | 1.8 | ×
Max hour / avg hour factor | 2.7 | × | 2.5-3.0 intermittent; 1.3-1.8 for 24×7 supply
UFW (NRW) allowance | 15 | %
OUTPUTS | VALUE | UNIT | FORMULA / NOTE
Average daily demand |  | m³/day | Q = Population × LPCD / 1000
Average daily demand |  | MLD
Maximum daily demand |  | m³/day | Q_max_day = factor × Q_avg · For source, raw-water main sizing
Maximum hourly demand |  | m³/hr | Q_peak_hr = pfHr × (Q_avg / 24) · For distribution pipe sizing
Fire demand (Kuichling) |  | L/min | Q_fire = 3182 × √(P/1000)
Design flow (distribution, with UFW + Fire) |  | m³/day | Q_design = Q_max_day × (1 + UFW%) + Q_fire × 4 hr
CPHEEO REFERENCE VALUES | STANDARD
LPCD urban+sewer | 135
LPCD urban no-sewer | 70
LPCD rural (JJM) | 55
Max-day factor | 1.8
Peak-hour factor | 2.5–3.0 (intermittent), 1.3–1.8 (24×7)
UFW design allowance | 15% (AMRUT/JJM target <20% actual)
Change the yellow INPUT cells — outputs recompute automatically. Formulas are live.