## Calculator
Hazen-Williams Pipe Sizing & Head Loss
Compute velocity and head loss for a given pipe using the Hazen-Williams equation. Standard Indian design basis for water supply transmission mains.
Generated by InfraLens · https://infralens.in/cpheeo · Based on CPHEEO Manual on Water Supply & Treatment (Govt of India, MoHUA)
INPUTS | VALUE | UNIT | HELP
Design flow Q | 500 | m³/hr | 500 m³/hr ≈ 12 MLD continuous
Internal diameter | 400 | mm
Pipe length | 1000 | m
Hazen-Williams C | 130 |  | DI new 130-140 · DI aged 100-110 · HDPE/PVC 150 · MS new 140
OUTPUTS | VALUE | UNIT | FORMULA / NOTE
Velocity |  | m/s | V = Q / A = (Q/3600) / (π×D²/4) · Target 0.6–2.5 m/s (1.0–1.5 economic optimum)
Hydraulic gradient |  | m/m | S = (V / (0.849 × C × R^0.63))^(1/0.54)
Head loss over length |  | m | h_f = S × L
Head loss per km |  | m/km
CPHEEO REFERENCE VALUES | STANDARD
Velocity range | 0.6 – 2.5 m/s
Economic velocity | 1.0 – 1.5 m/s
C — DI new | 130 – 140
C — HDPE / PVC | 150
C — Cast iron aged | 60 – 80
Change the yellow INPUT cells — outputs recompute automatically. Formulas are live.