## Calculator
WTP Dosing & Unit Sizing (Alum / Sedimentation / RSF)
Size coagulant dosing, sedimentation tanks, and rapid sand filters for a given WTP capacity. Based on CPHEEO Chapter 8 design parameters.
Generated by InfraLens · https://infralens.in/cpheeo · Based on CPHEEO Manual on Water Supply & Treatment (Govt of India, MoHUA)
INPUTS | VALUE | UNIT | HELP
Plant capacity | 10 | MLD
Alum dose | 30 | mg/L | Jar-test-determined, 20-40 mg/L typical for 50-200 NTU raw water
Sedimentation SLR | 1.5 | m³/m²/hr
Sedimentation retention | 3 | hr
RSF hydraulic loading | 6 | m/hr
Area per filter unit | 50 | m² | Standard filter unit size, 30-80 m² typical
OUTPUTS | VALUE | UNIT | FORMULA / NOTE
Alum consumption |  | kg/day | Mass = MLD × dose(mg/L) [since 1 MLD × 1 mg/L = 1 kg/day]
Sedimentation tank area |  | m² | A = Q / SLR = (MLD × 10⁶ / 86400) / SLR
Sedimentation tank volume |  | m³ | V = Q × retention = (MLD × 10⁶ / 86400) × t × 3600
Total RSF area required |  | m² | A = Q / HLR
Number of filter units |  | units | N = ⌈Total area / unit area⌉ + 1 standby · Round up; add one for standby during backwash
CPHEEO REFERENCE VALUES | STANDARD
Alum dose typical | 20 – 40 mg/L
Sedimentation SLR | 1.0 – 2.5 m³/m²/hr
Retention time | 3 – 4 hr
RSF HLR | 5 – 7 m/hr
Sand depth | 600 – 750 mm (eff. size 0.4–0.7 mm)
Change the yellow INPUT cells — outputs recompute automatically. Formulas are live.