## Calculator
Chlorine Dose — Gas · Bleaching Powder · NaOCl
Compute daily chlorine requirement for any plant capacity and convert to the three common chlorine forms used in Indian water supply.
Generated by InfraLens · https://infralens.in/cpheeo · Based on CPHEEO Manual on Water Supply & Treatment (Govt of India, MoHUA)
INPUTS | VALUE | UNIT | HELP
Flow | 10 | MLD
Chlorine dose | 2 | mg/L | Demand 0.5-1.5 mg/L + Residual 0.5-1.0 mg/L
Bleaching powder strength | 30 | % | Available chlorine; 30-35% standard
NaOCl solution strength | 5 | % | 5% typical field-diluted, 10% commercial bulk
Contact time | 30 | min
OUTPUTS | VALUE | UNIT | FORMULA / NOTE
Chlorine (gas) required |  | kg/day | kg/day = MLD × dose(mg/L)
Bleaching powder required |  | kg/day | kg/day = Cl₂ / (strength%/100)
NaOCl solution required |  | L/day | L/day = Cl₂ / (strength% × 10) [10 g/L per 1% approx]
Contact tank volume |  | m³ | V = Q × t / 60 · Ensures minimum 30 min contact time
CT value (residual × time) |  | mg.min/L | CT = residual × contact (residual ≈ dose × 0.3 after demand satisfied) · Target ≥ 15 for E.coli, ≥ 30 for virus
CPHEEO REFERENCE VALUES | STANDARD
Dose typical | 1.0 – 2.5 mg/L
Residual at WTP outlet | 0.5 – 1.0 mg/L
Residual at consumer | 0.2 – 0.5 mg/L
Contact time minimum | 30 min
Bleaching powder strength | 30 – 35% available Cl
Change the yellow INPUT cells — outputs recompute automatically. Formulas are live.