## Calculator
Distribution Pipe Check — Velocity, Head Loss, Residual Pressure
Verify a proposed distribution pipe against CPHEEO velocity limits (0.6–2.4 m/s) and compute residual pressure at the downstream end.
Generated by InfraLens · https://infralens.in/cpheeo · Based on CPHEEO Manual on Water Supply & Treatment (Govt of India, MoHUA)
INPUTS | VALUE | UNIT | HELP
Peak hour flow | 50 | m³/hr
Pipe diameter | 150 | mm
Pipe length | 500 | m
Hazen-Williams C | 130
Inlet pressure head | 30 | m | Pressure at upstream end (m water column)
Elevation rise to outlet | 5 | m | Negative if downhill
OUTPUTS | VALUE | UNIT | FORMULA / NOTE
Velocity |  | m/s | V = Q / A · Must be 0.6 – 2.4 m/s
Head loss (friction) |  | m | Hazen-Williams
Residual pressure at outlet |  | m | P_out = P_in − h_f − elevation rise · Consumer min 7 m · Ferrule min 17 m
CPHEEO REFERENCE VALUES | STANDARD
Velocity range | 0.6 – 2.4 m/s
Residual pressure (consumer) | 7 m minimum
Residual pressure (ferrule) | 17 m minimum
Maximum operating pressure | 70 m (7 bar)
Change the yellow INPUT cells — outputs recompute automatically. Formulas are live.