## Calculator
Pump Power, Energy & Annual Cost
Compute hydraulic, shaft, and input power + daily/annual energy + operating cost for a water-supply pump set. Formula P = Q × H / (367 × η).
Generated by InfraLens · https://infralens.in/cpheeo · Based on CPHEEO Manual on Water Supply & Treatment (Govt of India, MoHUA)
INPUTS | VALUE | UNIT | HELP
Flow Q | 200 | m³/hr
Total Dynamic Head | 50 | m | Static lift + friction + residual
Pump efficiency | 0.75 |  | New pump 0.80 BEP; aged 0.65
Motor efficiency | 0.93 |  | IE3 = 0.93; IE4 = 0.95
Running hours per day | 20 | hr
Electricity tariff | 8 | ₹/kWh
OUTPUTS | VALUE | UNIT | FORMULA / NOTE
Hydraulic power |  | kW | P_hyd = Q × H / 367
Shaft power |  | kW | P_shaft = P_hyd / η_pump
Input electrical power |  | kW | P_in = P_shaft / η_motor · Specify next-standard motor size (e.g., 15 → 18.5 kW)
Daily energy |  | kWh/day
Annual energy |  | kWh/yr
Annual electricity cost |  | ₹/yr
Specific energy |  | kWh/m³ | SE = input_kW / Q · Benchmark 0.25 – 0.50 kWh/m³ for urban water pumping
CPHEEO REFERENCE VALUES | STANDARD
Pump efficiency new | 0.75 – 0.88 at BEP
Motor efficiency IE3 | 0.92 – 0.95
Specific energy urban | 0.25 – 0.50 kWh/m³
VFD savings | 20–40% vs throttled fixed-speed
Change the yellow INPUT cells — outputs recompute automatically. Formulas are live.