## Calculator
NRW · Minimum Night Flow · ILI Dashboard
Quantify Non-Revenue Water, estimate real losses from minimum night flow, and compute Infrastructure Leakage Index (ILI) against the IWA world-class benchmark.
Generated by InfraLens · https://infralens.in/cpheeo · Based on CPHEEO Manual on Water Supply & Treatment (Govt of India, MoHUA)
INPUTS | VALUE | UNIT | HELP
Annual production | 3650 | ML/year | Total water produced
Annual billed consumption | 2200 | ML/year
Network length | 150 | km
Number of service connections | 25000
Average operating pressure | 30 | m
Minimum Night Flow | 80 | m³/hr | Measured at 2-4 AM via DMA inlet meter
Average hourly flow | 400 | m³/hr
OUTPUTS | VALUE | UNIT | FORMULA / NOTE
NRW |  | % | NRW% = (Production − Billed) / Production × 100 · AMRUT/JJM target < 20% · Indian avg 35–45%
Estimated real losses |  | ML/year | Real loss ≈ 70% of NRW (balance = apparent losses)
UARL (unavoidable annual real losses) |  | ML/year | UARL = (18×L + 0.8×N) × P × 365 / 1000 [simplified IWA]
ILI (Infrastructure Leakage Index) |  |  | ILI = Real losses / UARL · < 2 world-class · 2–4 good · 4–8 average · > 8 poor
MNF as % of average |  | % | MNF/Avg × 100 · 5–10% healthy · 20–40% indicates leakage
Background leakage (from MNF) |  | m³/day | Leakage ≈ (MNF − legitimate night use 5–10%) × 24 · Assumes 7% legitimate night use
CPHEEO REFERENCE VALUES | STANDARD
NRW world-class | < 10%
NRW AMRUT/JJM target | < 20%
NRW Indian urban avg | 35 – 45%
ILI world-class | < 2
ILI Indian typical | 8 – 15
Change the yellow INPUT cells — outputs recompute automatically. Formulas are live.